## Slide 1
Return Air
Supply Air
Psychrometric Chamber
Mix with air from Nozzle
Return Air Temp.
Low Coil Temp.
MED Coil Temp.
Reheat Coil Temp.
Low Temp. Coils A & B
Medium Temp. Coils C & D
Electric Heater
VFD
MED Coil
LOW Coil
Fan speed in Hz and power
Measure: room temperature using room sensor and 9-thermocouple grid below Midea unit
All measurements:
Return air temperature
Air temperature after low-temp. coil
Air temperature after medium-temp. coil
Air temperature after heater coil
Differential pressure across low-temp coil
Differential pressure across medium-temp coil
VFD speed and power
Chamber room temperature
Control: reheater capacity from 0% to 100%
Control: cooling coil suction temperature